## BR
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
BR-1 | Where pipework has either been replaced, exposed, or been made accessible as part of the work within an unheated space within the building envelope, has this been insulated? | BR | Y | Pass / Fail / NA
BR-2 | Does the boiler produce hot water for the central heating system? | BR | Y | Pass / Fail
BR-3 | If the boiler is designed to produce domestic hot water, is the boiler producing domestic hot water? | BR | Y | Pass / Fail / NA
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Location of boiler identifying the room and its position in the room
Electric supply to boiler and fixed fused spur
Bonding at boiler
Bonding at meter
Internal path of flue (Including any compartmentalised areas)
All exposed pipework showing insulation in place
Flue termination externally
PRV termination
Condensate termination (N.B. maybe internal)
Condensate diameter through wall
Condensate pipework externally (diameter and show insulated along the full length of external run)
Condensate termination (e.g. into gully /pipe/ soakaway)
Presence of CO Detector (where required)
Presence of Frost stat (where required)
Photograph of location and prescence of thernostat and programmer (show make and model)
Photograph showing location of bypass radiator
Photograph of all other radiators showing presence of TRV's
Documents:
Householder declaration to confirm they understand how to use controls
Householder documentation to confirm that the controls turn on the domestic heating system

## NB
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
NB-1 | Where pipework has either been replaced, exposed, or been made accessible as part of the work within an unheated space within the building envelope, has this been insulated? | New Boiler | Y | Pass / Fail / NA
NB-2 | If holes or openings have been made through the fabric of the premises due to the installation of a new boiler, have they been made good? (including condensate pipe, pressure relief valve, gas flue terminals) | New Boiler | Y | Pass / Fail / NA
NB-3 | Does the boiler produce hot water for the central heating system? | New Boiler | Y | Pass / Fail / NA
NB-4 | If the boiler is designed to produce domestic hot water, is the boiler producing domestic hot water? | New Boiler | Y | Pass / Fail / NA / Unable to validate
NB-5 | If original heating controls remain, do they function correctly with the boiler? | New Boiler | Y | Pass / Fail / NA / Unable to validate
NB-6 | Do the heating controls installed encompass a programmer, thermostat and TRVs to all radiators except those in the room with the thermostat? | New Boiler | Y | Pass / Fail / NA / Unable to validate
HSNB-1 | Has a carbon monoxide detector been provided in line with Scottish Building Regulations? | New Boiler | Y | Pass / Fail / NA
HSNB-2 | Has the boiler been installed as per manufacturer’s instructions and other guidance? | New Boiler | Y | Pass / Fail
HSNB-3 | Do any faults specific to the measure installed present an immediate risk to the occupier? | New Boiler | Y | Pass / Fail
HSNB-4 | Do you believe there are no other safety related issues with the installation? | New Boiler | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Location of boiler identifying the room and its position in the room
Electric supply to boiler and fixed fused spur
Bonding at boiler
Bonding at meter
Internal path of flue (Including any compartmentalised areas)
All exposed pipework showing insulation in place
Flue termination externally
PRV termination
Condensate termination (N.B. maybe internal)
Condensate diameter through wall
Condensate pipework externally (diameter and show insulated along the full length of external run)
Condensate termination (e.g. into gully /pipe/ soakaway)
Presence of CO Detector (where required)
Presence of Frost stat (where required)
Photograph of location and prescence of thernostat and programmer (show make and model)
Photograph showing location of bypass radiator
Photograph of all other radiators showing presence of TRV's
Documents:
Householder declaration to confirm they understand how to use controls
Householder documentation to confirm that the controls turn on the domestic heating system

## HC
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
HC-1 | Are the heating controls, smart thermostat or TRVs (whichever is applicable) linked to a functioning heating system? | HC | Y | Pass / Fail
HC-2 | Do the heating controls or smart thermostat turn on the domestic heating system? | HC | Y | Pass / Fail
HSHC-1 | Has the control been installed as per manufacturer’s instructions and other guidance? | HC | Y | Pass / Fail
HSHC-2 | Do any faults specific to the measure installed present an immediate risk to the occupier? | HC | Y | Pass / Fail
HSHC-3 | Do you believe that there are no other safety related issues with the installation? | HC | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Location of boiler identifying the room and its position in the room
Photograph of location and prescence of thernostat and programmer (show make and model)
Photograph showing location of bypass radiator
Photograph of all other radiators showing presence of TRV's
Documents:
Householder declaration to confirm they understand how to use controls
Householder documentation to confirm that the controls turn on the domestic heating system

## NESH
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
ESHR-1 | Is the repair to an Electric Storage Heater as opposed to a panel heater or other kind of heater? | ESHR | Y | Pass / Fail
ESHR-2 | Does the Electric Storage Heater activate and produce heat? | ESHR | Y | Pass / Fail / Unable to validate
ESHR-3 | Is the property on an Economy 7 or differential off-peak tariff? | ESHR | Y | Pass / Fail / Unable to validate
ESHR-4 | Where the property is on a differential off-peak tariff, are the Electric Storage Heaters connected to a separate consumer unit? | ESHR | Y | Pass / Fail / Unable to validate
HSESH-1 | Has the ESH been installed as per manufacturer’s instructions and other guidance? | ESH | Y | Pass / Fail
HSESH-2 | Do any faults specific to the measure installed present an immediate risk to the occupier? | ESH | Y | Pass / Fail
HSESH-3 | Do you believe that there are no other safety related issues with the installation? | ESH | Y | Pass / Fail
NESH-1 | Is the installation an Electric Storage Heater as opposed to a panel heater or other kind of heater? | NESH | Y | Pass / Fail
NESH-2 | Does the Electric Storage Heater activate and produce heat? | NESH | Y | pass_fail_utv
NESH-3 | Are all storage heaters fitted with an automatic charge control? | NESH | Y | pass_fail_utv
NESH-4 | Is the fan on fan-assisted storage heater(s) controlled by a thermostat? | NESH | Y | Pass / Fail
NESH-5 | Is the property on an Economy 7 or differential off-peak tariff? | NESH | Y | Pass / Fail / Unable to validate
NESH-6 | Where the property is on a differential off-peak tariff, are the Electric Storage Heaters connected to a separate consumer unit? | NESH | Y | Pass / Fail / NA / Unable to validate
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Photograph of meter and any evidence that household is on Economy 7 tariff or differential off peak tariff
Photograph of separate consumer (if on Differential off-peak tariff)
Location of ESH identifying the room and its position in the room (must show appropriate siting (including feet resting in level position inline with MI, adequate fixing, wiring and adequate clearances and make and model of each heat emitter)
If fan- assisted – photograph of thermostat
Floor plan illustrating location of ESH
Electric switched spur for each heat emitter showing condition and secure wiring
Documents:
MEIWC (Minor Electrical Installation Work Certificate)
Current electric bill to confirm tariff

## ESHR
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
ESHR-1 | Is the repair to an Electric Storage Heater as opposed to a panel heater or other kind of heater? | ESHR | Y | Pass / Fail
ESHR-2 | Does the Electric Storage Heater activate and produce heat? | ESHR | Y | Pass / Fail / Unable to validate
ESHR-3 | Is the property on an Economy 7 or differential off-peak tariff? | ESHR | Y | Pass / Fail / Unable to validate
ESHR-4 | Where the property is on a differential off-peak tariff, are the Electric Storage Heaters connected to a separate consumer unit? | ESHR | Y | Pass / Fail / Unable to validate
HSESH-1 | Has the ESH been installed as per manufacturer’s instructions and other guidance? | ESH | Y | Pass / Fail
HSESH-2 | Do any faults specific to the measure installed present an immediate risk to the occupier? | ESH | Y | Pass / Fail
HSESH-3 | Do you believe that there are no other safety related issues with the installation? | ESH | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Photograph of meter and any evidence that household is on Economy 7 tariff or differential off peak tariff
Photograph of separate consumer if on Differential off-peak tariff)
Location of ESH identifying the room and its position in the room (must show appropriate siting (including feet resting in level position inline with MI, adequate fixing, wiring and adequate clearances and make and model of each heat emitter)
If fan- assisted – photograph of thermostat
Floor plan illustrating location of ESH
Electric switched spur for each heat emitter showing condition and secure wiring
Documents:
MEIWC (Minor Electrical Installation Work Certificate)
Current electric bill to confirm tariff

## CWI
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insulated, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
CWI-1 | Is the insulation material suitable for use with the property’s exposure level to wind driven rain? | CWI | Y | Pass / Fail
CWI-2 | Does the form of the construction of the property suggest that it was suitable for the material that has been installed? | CWI | Y | Pass / Fail
CWI-3 | Does the current condition of the property suggest that it was suitable for the material that has been installed? | CWI | Y | Pass / Fail
CWI-4 | Does the drilling pattern conform to the appropriate materials compliance certificate? | CWI | Y | Pass / Fail / Unable to validate
CWI-5 | Have all injection holes been filled? | CWI | Y | Pass / Fail / Unable to validate
CWI-6 | Have all vents been safeguarded and have redundant vents been sealed? | CWI | Y | Pass / Fail / NA
CWI-7 | Is there any evidence of the escape of insulation? | CWI | Y | Pass / Fail
CWI-8 | Are there any signs of damp or condensation? | CWI | Y | Pass / Fail
CWI-9 | If the cavity wall contains pre-existing insulation, is the additional insulation to be added compatible with the pre-existing insulation as demonstrated by the product certificate? | CWI | N | Pass / Fail
HSCWI-1 | Are combustion vents/flues/chimneys clear of insulation and in compliance with HSE/CIGA guidance? | CWI | Y | Pass / Fail / NA
HSCWI-2 | Have combustion air core vents been fitted where required? | CWI | Y | Pass / Fail / NA
HSCWI-3 | Are all the air bricks and eaves vents clear of insulation material and sleeves installed where appropriate? | CWI | Y | Pass / Fail / NA
HSCWI-4 | Do any faults specific to the measure installed present an immediate risk to the occupier? | CWI | Y | Pass / Fail
HSCWI-5 | Do you believe that there are no other safety related issues with the installation? | CWI | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front door showing door number
Front door open
Elevations - all required - taken front on where possible, include any return walls.
Front and rear elevation to show full height to ridge line including guttering and downpipes
DPC - photo of each elevation showing the DPC and its height above the ground level (including prescence of any features such as adjacent decking, slopes, raised beds, soakaways etc).
Vents - photos of each combustion ventilation, if applicable, floor and wall vents
Trickle vents in windows and any other type of extractor fan
Guttering and downpipes - all elevations
Loft showing internal wall substrate and cavity head
Loft showing eaves clear of insulation and cavity head
Primary heating source
Secondary heating source showing rating plates and location of flues / chimneys
Tertiary heating source (if present)
Photograph of location fo any redundant flues
Internal rooms and external heat loss walls
Building defects including spalled, damaged brickwork and cracks
Ivy and any other vegitation on property
Close up of all waste pipes exiting through the cavity to check seal around pipes
Working at height issuees - for example, conservatory
Omitted areas not to be filled
Gas meter box
Inside electric meter box
Any other obstructions exiting through the cavity, for example, cables, extractor fans etc

## EWI
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
EWI-13 | Where services (e.g. gas, electric, water, telecommunications) have penetrated the insulation board have these been sealed appropriately? | EWI | Y | Pass / Fail / NA
EWI-14 | Are there any visible signs of water penetration? | EWI | Y | Pass / Fail
EWI-15 | Has the render/cladding been fully applied? | EWI | Y | Pass / Fail
EWI-16 | Where appropriate, have window and door reveals been insulated in line with the system designers specifications? | EWI | Y | Pass / Fail / NA
EWI-17 | Have all exterior facing wall areas (above DPC) been insulated in line with the system designers specifications to reduce the effects of thermal bridging? | EWI | Y | Pass / Fail / NA / Unable to validate
EWI-18 | Have all exterior window and door seals been applied and finished off in line with the system designers specifications? | EWI | Y | Pass / Fail / NA / Unable to validate
EWI-19 | Where necessary, has the roofline been extended in line with the system designers specifications to cover the EWI works and prevent water ingress? | EWI | Y | Pass / Fail / NA
EWI-20 | Is there evidence of damage to the EWI fabric as a result of water ingress? | EWI | Y | Pass / Fail
HSEWI-2 | Where required have air supply vents been installed for combustion appliances? | EWI | Y | Pass / Fail / NA
HSEWI-4 | Has adequate provision been made to safeguard, relocate or provide access to gas/electric/water/telecomms/TV services? | EWI | Y | Pass / Fail / NA
HSEWI-5 | Can all doors and windows still be fully opened? | EWI | Y | Pass / Fail
HSEWI-6 | Are all the air bricks clear of insulation material? | EWI | Y | Pass / Fail / NA
HSEWI-7 | Do any faults specific to the measure installed present an immediate risk to the occupier? | EWI | Y | Pass / Fail
HSEWI-8 | Do you believe that there are no other safety related issues with the installation? | EWI | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Side and rear elevation to give context
Any areas not treated
Combustion appliances identifying kW rating
All combustion vents
Photographs of mechanical ventilation present in all wetrooms
Photographs of adequate heating present in all wet rooms that are untreated
Photographs of air-bricks showing they are clear of insulation
Photographs of the DPC line (if visible)
Photographs of the roof line showing junctions an covering of EWI system
Photograph of installers carded operative scheme card (C2 only)
Photographs of boarding and fixing patters (pre-scrim coat) all elevations (C2 only)
Close up photograph of treatment around boiler flues and combustion vents (at C2 and C3 stage where appropriate)
Photograph of fire barriers (C2 only)
Photographs of all external features (including but not limited too, satellite dishes, fences, door canopies, alarm boxes, gas and other utility supply pipes and meter boxes, electric and comms cabling, external lighting, down comers and etc) (at C2 and C3 stage where appropriate)
Photographs of all utility penetrations (including but not limited too, flues and vents, PRV termination, condensate pipes, drainage and sol pipes etc)
Photographs showing the base of the EWI system is sealed appropriately and in in with manufacturers instructions
Photographs of all window and reveals showing insulation in situ and appropriate sealing
Photographs showing air bricks are clear of insulation material
Documents:
PIBI (For both Question EWI-2 and to assist in reviewing any treatment of thermal bridges)
System Designer specification

## IWI
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
IWI-2 | If the measure is being installed, is it being installed as specified in the appropriate product certificate and/or system designer's instructions? If the measure is installed, was it installed as specified in the appropriate product certificate and/or system designer's instructions? | IWI | Y | Pass / Fail
IWI-7 | Is the insulation sealed around all adjoining boards, walls, ceilings and floors? | IWI | Y | Pass / Fail / Unable to validate
IWI-8 | Is the insulation continued 400mm along all party and solid partition walls? | IWI | Y | Pass / Fail / NA
IWI-9 | Have all services (e.g. light switches, sockets, radiators) been removed, insulated behind and re-positioned inside the heat loss area? | IWI | Y | Pass / Fail / NA
IWI-10 | Has the system been sealed fully at edges, corners and junctions to prevent the ingress of moisture? | IWI | Y | Pass / Fail
HSIWI-2 | Where required have air supply vents been installed for combustion appliances? | IWI | Y | Pass / Fail / NA
HSIWI-3 | Have all flues, chimneys and ventilation air supplies for combustion appliances been safeguarded? | IWI | Y | Pass / Fail / NA
HSIWI-4 | Has adequate provision been made to safeguard, relocate or provide access to gas/electric/water/telecomms/TV services? | IWI | Y | Pass / Fail / NA
HSIWI-5 | Can all doors and windows still be fully opened? | IWI | Y | Pass / Fail / NA
HSIWI-6 | Are all the air bricks clear of insulation material? | IWI | Y | Pass / Fail / NA
HSIWI-7 | Where required have air supply vents been installed for combustion appliances? | IWI | Y | Pass / Fail / NA
HSIWI-8 | Do any faults specific to the measure installed present an immediate risk to the occupier? | IWI | Y | Pass / Fail
HSIWI-9 | Do you believe that there are no other safety related issues with the installation? | IWI | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Side and rear elevation to give context to floor plan
Floor plan showing areas treated and highlighted any areas not treated
Photographs of any areas not treated
Photographs of combustion appliances identifying kW rating
Photographs of all combustion vents
Photographs of mechanical ventilation present in all wetrooms
Photographs of adequate heating present in all wet rooms that are untreated
Photographs of air-bricks showing they are clear of insulation
Photograph of installers carded operative scheme card (C2 only)
Photographs showing the base of the IWI system fitted securely to the floor level and sealed appropriately
Photographs of all features (e.g radiators, sockets, switches, coving, recessed cupboards showing they are insulated appropriately)
Photographs of all window reveals showing insulation in situ
Photographs showing 400mm return along solid partition and party walls or valid statement explaining why not undertaken
Photograph showing insulation of inter-floor void or valid statement explaining why not undertaken

## RIRI
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
RIRI-1 | Has insulation been installed to all stud walls within the room in the roof? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-2 | Has insulation been installed to all sloping ceilings within the room in the roof? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-3 | Has insulation been installed to the ceiling within the room in the roof? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-4 | Has insulation been installed to all dormer windows cheek walls and ceilings within the room-in-roof? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-5 | Where down lighters or services have been fitted through the existing ceiling, have any measures been taken to prevent air leakage around down lights into the roof void? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-6 | Has insulation been installed to all party walls within the room-in-roof that are either cavity walls or solid walls bordering an unheated space? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-7 | Have any tanks or pipework present in the residual area been insulated? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-8 | Have all hatches installed as part of the room-in-roof insulation been insulated as specified in the relevant annex of PAS? | RIRI | Y | Pass / Fail / NA / Unable to validate
RIRI-9 | Has insulation been installed to all gable walls within the room-in-roof? | RIRI | Y | Pass / Fail / NA / Unable to validate
HSRIR-1 | Has the measure been installed in accordance with PAS2030? | RIRI | Y | Pass / Fail
HSRIR-3 | Where required have air supply vents been installed for combustion appliances? | RIRI | Y | Pass / Fail / NA
HSRIR-4 | Have all flues, chimneys and ventilation air supplies for combustion appliances been safeguarded? | RIRI | Y | Pass / Fail / NA
HSRIR-5 | Has adequate provision been made to safeguard, relocate or provide access to gas/electric/water/telecomms/TV services? | RIRI | Y | Pass / Fail / NA
HSRIR-6 | Can all doors and windows still be fully opened? | RIRI | Y | Pass / Fail
HSRIR-7 | Are all the air bricks clear of insulation material? | RIRI | Y | Pass / Fail / NA
HSRIR-8 | Where required have air supply vents been installed for combustion appliances? | RIRI | Y | Pass / Fail / NA
HSRIR-9 | Do any faults specific to the measure installed present an immediate risk to the occupier? | RIRI | Y | Pass / Fail
HSRIR-10 | Do you believe that there are no other safety related issues with the installation? | RIRI | Y | Pass / Fail
HSRIR-12 | Are downlights safeguarded in accordance with PAS2030? | RIRI | Y | Pass / Fail / NA
HSRIR-13 | Are other electrical apparatus penetrating the ceiling safeguarded in accordance with PAS2030? | RIRI | Y | Pass / Fail / NA
HSRIR-14 | Is there clearance between the insulation and flues and chimneys in accordance with PAS2030? | RIRI | Y | Pass / Fail / NA
HSRIR-15 | Have all essential ventilation openings been safeguarded in accordance with PAS 2030? | RIRI | Y | Pass / Fail / NA
HSRIR-16 | Is a walkboard fitted in accordance with PAS2030? | RIRI | Y | Pass / Fail / NA
HSRIR-17 | Are warning signs fitted in accordance with PAS2030? | RIRI | Y | Pass / Fail / NA
HSRIR-18 | Do any faults specific to the measure installed present an immediate risk to the occupier? | RIRI | Y | Pass / Fail
HSRIR-19 | Do you believe that there are no other safety related issues with the installation? | RIRI | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Side and rear elevation to give context to floor plan
Floor plan showing areas treated and highlighted any areas not treated
Photographs of any areas not treated
Photographs of combustion appliances identifying kW rating
Photographs of all combustion vents
Photographs of mechanical ventilation present in all wetrooms
Photographs of adequate heating present in all wet rooms that are untreated
Photographs of air-bricks showing they are clear of insulation
Photographs of all windows and doors in the RIR
Photographs of the fixed stiarway to the RIR
Photographs of the gable walls including any corridors
Photographs of residual areas showing levels of insulation, pipework etc
Photographs of stud walls showing prescence of hatches (hatch closed)
As above but with hatch open showing insulation on back of hatch and draughtproofing)
Photographs of dormer windows showing insulated cheeks and flat ceiling
(Note: for the above you may supply mid-installation photographs)
Mid-instalation photogrpahs for any areas completely sealed or covered by insulation
Documents:
Floor plan showing number of rooms in RIRI
PIBI
Where IWI solution is deployed
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Side and rear elevation to give context to floor plan
Floor plan showing areas treated and highlighted any areas not treated
Photographs of any areas not treated
Photographs of combustion appliances identifying kW rating
Photographs of all combustion vents
Photographs of mechanical ventilation present in all wetrooms
Photographs of adeqwate heating present in all wet rooms that are untreated
Photographs of air-bricks showing they are clear of insulation
Photograph of installers carded operative scheme card (C2 only)
Photographs showing the base of the IWI system fitted securely to the floor level and sealed appropriately
Photographs of all features (e.g radiators, sockets, switches, coving, recessed cupboards showing they are insulated appropriately)
Photographs of all window reveals showing insulation in situ
Photographs showing 400mm return along solid partition and party walls or valid statement explaining why not undertaken
Photograph showing insulation of inter-floor void or valid statement explaining why not undertaken
Where LI solution is deployed
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Loft hatch closed
Loft hatch open
Loft hatch rebate showing prescence of draughtproofing
Back of loft hatch showing insulation (including measurement of correct depth)
Various photos showing all angles of the loft space
Clear measurement of the insulation thickness
Original insulation
Ceiling photos to show all parts of underside of loft area – to identify lighting
Bathroom and shower photo (include electric shower cord pull location)
Photographs of mechanical ventilation present in all wetrooms
Airing cupboard door open (showing ceiling with any penetrating pipework)
Roof outside (each elevation)
External elevation photos (all elevations)
Ridges and tile vents (if applicable)
Pipes in loft
Tanks in loft
Roof lining (enough photos to show all parts of roof)
Exposed timbers
F rated caps if fitted
Warning and Notification signs fixed to roof joists

## FRI
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
FRI-5 | Is there any evidence of water penetration? | FRI | Y | Pass / Fail / Unable to validate
FRI-6 | Has a waterproof membrane been applied over the whole of the insulated area, including ‘Up Stands’ after the laying of the insulation board? | FRI | Y | Pass / Fail
FRI-7 | Has the area between the wall and flat roof slab been insulated to prevent cold bridging? | FRI | Y | Pass / Fail / NA / Unable to validate
HSFRI-1 | Has the Flat Roof measure been installed as per manufacturer's instructions and other guidance? | FRI | Y | Pass / Fail
HSFRI-2 | Are electrical cables safeguarded in accordance with PAS 2030? | FRI | Y | Pass / Fail / NA
HSFRI-3 | Are down lights safeguarded in accordance with PAS 2030? | FRI | Y | Pass / Fail / NA
HSFRI-4 | Are other electrical apparartus penetrating the ceiling safeguarded in accordance with PAS2030? | FRI | Y | Pass / Fail / NA
HSFRI-5 | Is the clearance between the insulation and flues and chimneys in accordance with PAS2030? | FRI | Y | Pass / Fail / NA
HSFRI-6 | Have all essential ventilation openings been safeguarded in accordance with PAS 2030? | FRI | Y | Pass / Fail / NA
HSFRI-7 | Have all flues chimneys and air supply vents for combustion appliances been safeguarded? | FRI | Y | Pass / Fail / NA
HSFRI-8 | Where required have air supply vents been installed for combustion appliances? | FRI | Y | Pass / Fail / NA
HSFRI-9 | Do any faults specific to the measure installed present an immediate risk to the occupier? | FRI | Y | Pass / Fail
HSFRI-10 | Do you believe that there are no other safety related issues with the installation? | FRI | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Side and rear elevation to give context
Any areas not treated
Combustion appliances identifying kW rating
All combustion vents
Photographs of mechanical ventilation present in all wetrooms
Photographs of adequate heating present in all wet rooms that are untreated
Photographs of air-bricks showing they are clear of insulation
Photpgraphs of entire rooftop showing waterproof membrane at all edges
Photographs showing all abutments illustrating butting together of boards at mid-installation stage
Photograph showing any upstands with tape measure in photograph to show depth
Evidence of cavity trays being raised or new ones installed at abutment of roof and wall
Photpgraphs of areas insulated between the wall and flat roof slab
Photpgrahs of treatment around any other rooftop features such as skylights, ducting or flues.
electronic leak detection certificate, conducted for guarantee
correctly fitted finishing trim at perimeter edges ensuring membrane secured to roof slab both adhesively and mechanically, allowing no water ingress from base of membrane.
sealed joints to membrane surface

## LI
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
LI-1 | Is the thickness of insulation consistent throughout the loft area? | LI | Y | Pass / Fail / Unable to validate
LI-2 | Has insulation been close butted? | LI | Y | Pass / Fail / Unable to validate
LI-3 | Has insulation been cross laid to prevent cold bridging? | LI | Y | Pass / Fail / Unable to validate
LI-4 | Has the loft hatch been insulated as specified in in the relevant PAS annex? | LI | Y | Pass / Fail / NA / Unable to validate
LI-5 | Has the loft hatch been draught proofed as specified in the relevant PAS annex? | LI | Y | Pass / Fail / NA / Unable to validate
LI-6 | Where down lighters or services have been fitted through the existing ceiling, have any measures been taken to prevent air leakage around down lights into roof void? | LI | Y | Pass / Fail / NA
LI-7 | Have any and all working pipes and tanks been properly insulated? | LI | Y | Pass / Fail / NA / Unable to validate
HSLI-1 | Are electric cables safeguarded in accordance with PAS2030? | LI | Y | Pass / Fail / NA
HSLI-2 | Are downlights safeguarded in accordance with PAS2030? | LI | Y | Pass / Fail / NA
HSLI-3 | Are other electrical apparatus penetrating the ceiling safeguarded in accordance with PAS2030-2012? | LI | Y | Pass / Fail / NA
HSLI-4 | Is there clearance between the insulation and flues and chimneys in accordance with PAS2030? | LI | Y | Pass / Fail / NA
HSLI-5 | Have all essential ventilation openings been safeguarded in accordance with PAS 2030? | LI | Y | Pass / Fail / NA
HSLI-6 | Is a walkboard fitted in accordance with PAS2030? | LI | Y | Pass / Fail / NA
HSLI-7 | Are warning signs fitted in accordance with PAS2030? | LI | Y | Pass / Fail / NA
HSLI-8 | Do any faults specific to the measure installed present an immediate risk to the occupier? | LI | Y | Pass / Fail
HSLI-9 | Do you believe that there are no other safety related issues with the installation? | LI | Y | Pass / Fail
Photo Evidence |  | Yes / No
Front elevation to include door number and open front door
Loft hatch closed
Loft hatch open
Loft hatch rebate showing prescence of draughtproofing
Back of loft hatch showing insulation (including measurement of correct depth)
Various photos showing all angles of the loft space
Clear measurement of the insulation thickness
Original insulation
Ceiling photos to show all parts of underside of loft area – to identify lighting
Bathroom and shower photo (include electric shower cord pull location)
Photographs of mechanical ventilation present in all wetrooms
Airing cupboard door open (showing ceiling with any penetrating pipework) and closed (why closed?)
Roof outside (each elevation)
External elevation photos (all elevations) same as above?)
Ridges and tile vents (if applicable)
Pipes in loft
Tanks in loft
Roof lining (enough photos to show all parts of roof)
Exposed timbers
F rated caps if fitted
Warning and Notification signs fixed to roof joists

## UFI
Question number | Question text | Measure | C3 | Result
TMQ1 | Have all avoidable thermal bridges/heat loss areas which could have been insualted, been insulated ? | ALL |  | Pass / Fail
TMQ2 | Has 100% of the measure been installed where possible? | ALL |  | Pass / Fail
UFI-1 | Is there a carded operative at the site that meets the competency requirements for the measure being installed? | UFI | Y | Pass / Fail / Unable to validate
UFI-2 | Is the measure/system being installed as specified in the appropriate product certificate and/or system designer's instructions? | UFI | Y | Pass / Fail
UFI-3 | Has insulation been close butted and laid in a break bond pattern on solid concrete floors? | UFI | Y | Pass / Fail / NA
UFI-4 | Has the insulation been tightly fixed between joists to avoid gaps? | UFI | Y | Pass / Fail
UFI-5 | Has the insulation been tightly fixed to the underside of the floor to avoid gaps? | UFI | Y | Pass / Fail
UFI-6 | Has insulation been installed in the gap between the last joist and external walls? | UFI | Y | Pass / Fail
UFI-7 | Has insulation been applied to working pipes below the insulation? | UFI | Y | Pass / Fail / NA
UFI-8 | Have all gaps in the floor around service penetrations been sealed? | UFI | N | Pass / Fail / NA
UFI-9 | For suspended floors, has insulation been applied to working pipes below the insulation? | UFI | N | Pass / Fail / NA / Unable to validate
HSUFI-1 | Has the under floor insulation in the property been installed as per manufacturer's instructions and other guidance? | UFI | Y | Pass / Fail
HSUFI-2 | Do any faults specific to the measure installed present an immediate risk to the occupier? | UFI | Y | Pass / Fail
HSUFI-3 | Do you believe that there are no other safety related issues with the installation? | UFI | Y | Pass / Fail
Photo Evidence |  | Yes / No
Adequate sub-floor cross flow ventilation has been provided
The air bricks are free from dust, vegetation and other impediments
The small gap between the last joists and the external walls are fully insulated.
Water pipework in the newly formed "cold space" is appropriately insulated image of thickness used which is located on the lagging.
The structure of the existing floor is suitable for the insulation i.e. no evidence of damp, rot etc
The underfloor area is free from pests and rodents
There are no existing leaks from pipework
Any combustion appliances in the space to be insulated have appropriate combustion ventilation in line with CIGA Guidance
Any pre-existing combustion vents that are due to be insulated are safeguarded in line with CIGA Guidance.
Any recessed floor lighting is safeguarded
Any high amperage cables (electric shower/cooker etc) that may be clipped to the underside of the floor joist are not covered by insulation
Any other in-situ equipment will not be compromised by the work undertaken
The insulation is applied in a manner which ensures that there are no exposed joists acting as thermal bridges this is dependant of joist thickness.
The insulation has been secured in position in line with system designer requirements.
Measurement of joist depth.
Photo of insulation thickness installed.
Measurement of gap from joist bottom to ground level in several areas.
Photos of overall install below the insulation showing 100% of area installed.
Photos of overall install below the insulation showing insulation is not sagging.
Cellar install images of fire rated sealants and plasterboards installed.